[image: image1.png]



Main Office & Warehouse
1681 W. Second St.
Pomona, CA  91766 
Tel: 626-797-9710  Fax: 626-798-4659

WWW.DAWSONCO.COM

Centrifugal Pump Pre-Startup Checklist
	Technician’s Name:      
	Date:       

	Pump Tag Number:       

	Pump Application:       


	This checklist is not a substitute for reading and implementing the safety measures and precautions as set forth in the Bell & Gossett I, O& M manuals.  Regardless of manufacturer, the instruction manual should be read and thoroughly understood before starting any pump.


	Item:
	Checked?
	Initials

	Electrical:

	-
	Motor leads connected per electrical code
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Motor starter leads connected
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Motor heaters sized correctly and installed
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Motor rotation and phase check and correct
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	Piping:

	-
	Proper suction pipe installed, 5 pipe diameters required
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	
	OR
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Suction diffuser installed
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	No pipe spring evidence
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Proper pipe anchors installed at change of direction
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Suction pipe support installed
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Suction and discharge flex connectors installed
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Suction and discharge isolation valves installed
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	Installation:

	-
	Pump located with sufficient maintenance room
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Pump base shimmed and leveled
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Pump base grouted
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	All foundation bolts installed with flat Type-W washers at each base plate anchor bolt hole location
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	Pump mounted on concrete foundation.  If isolation pad is used, refer to Hydraulic Institute Standards for recommendations
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	

	-
	System primed, air removed from pump casing
	 FORMCHECKBOX 
  Yes
	 FORMCHECKBOX 
  No
	


[image: image2.png]DAWSON CO.

EEEEEEEEEEEEEEEEEEEEEEEEEEE





Form#: DC-004-SVC-002


